## Sheet1
Measurement of Voltage and Current
(For any unbalance, monitoring, any short circuit fault, any overload) |  |  | Rated | Software | DIFF | % | Is it <= 1%?
| CHANNEL-A | IR (A) | 49.79 | 49.92 | -0.13 | -0.2611 | Yes
| CHANNEL-A | IY (A) | 49.78 | 49.91 | -0.13 | -0.26115 | Yes
| CHANNEL-A | IB (A) | 49.8 | 49.89 | -0.09 | -0.18072 | Yes
| CHANNEL-A | VR (V) | 259.05 | 259.15 | -0.1 | -0.038603 | Yes
| CHANNEL-A | VY (V) | 259.91 | 259.98 | -0.07 | -0.026932 | Yes
| CHANNEL-A | VB (V) | 264.4 | 264.52 | -0.12 | -0.045386 | Yes
Current trip test (Time in Sec):
For any overload
Current trip test (Current in Amps)
|  | Rated | Software | Difference
| R | 50.14 | 50.33 | 0.19
| Y | 50.13 | 50.34 | 0.21
| B | 49.81 | 49.98 | 0.17
| Observation noted: | Tripped by set current of 50 A.
Temperature based tripping
Tripping for more temperatures |  | Setting | Rated | Software | Difference
| 1 | 60 | 59.9 | 60.25 | 0.35
| 2 | 60 | 59.45 | 60 | 0.55
| 3 | 60 | 59.5 | 59.75 | 0.25
Oil Leakage |  | Rated level | Check of minimum level
(To check of leakage, sensor is required) |  | Volume of oil
Communication |  | GPRS and Master Number
(To intimate about status)
Implimentatio of AI for further descion making